## Sheet1
Common Fields
XB={sender}	Station id, eg. TWT, TRB, etc.	All packet types require this field
PT={packet type}	Specifies type of packet, eg. LVL is tank level, TRB is turbine status.	All packet types require this field
DST={destination}	Station id of desired reciever	Some packets require this field.

	Packet Type	Example	Desc
General Packets	PING: Ping request	~XB=VST,PT=PING~	All listening stations should respond with ping response
	PONG: Ping response	~XB=TRB,PT=PONG~	Emitted when unit receives a ping request
	TOD: Time of Day	~XB=VST,PT=TOD,H=21,M=49~	Webserver (VST) unit sends these to sync the time consuming stations, currently GTS and RDG
	LTR: Local time report	~XB=GTS,PT=LTR,H=12,M=45~	Emitted periodically by units that keep time; currently just for debugging, to see what time a unit thinks it is. GTS and RDG are the only time consumers as of this writing

Water Tank Packets	LVL: Water Tank Level / Emitted periodically, and when level change detected	~XB=FWT,PT=LVL,L=4~	L: The level, 0-6 (0-5 @ RDG), corresponding to height of water level in the in-service tanks

Turbine Packets	TRB: Turbine Status / Emittted Periodically	~XB=TRB,PT=TRB,V=AC ,P=201,M=0~	V: 4-character string, either 'NONE' or a list of currently open valves, eg. “ABC “ / P: psi / M: operating mode, 0 = auto, 1=manual
	VOP: Valve Operation / Emitted when a valve state changes	~XB=TRB,PT=VOP,VLV=A,OP=OPEN~	VLV: The valve in question, or 0 for all open/close msgs. / OP: The operation being performed. OPEN or CLOSE when VLV is being opened or closed, ALLO,ALLC when responding to step up/down command and all valves are already open/closed.
	AWK: Acknowldgement / Emitted when requested operation is complete	~XB=TRB,DST=VST,PT=AWK~	DST: The station that requested the operation
	SVS: Set Valve State / Instruction to change valve state	~XB=VST,DST=TRB,PT=SVS,VS=4~	VS: Valve State, 0 (all closed) to 7 (A,B, and C open)
	SCM: Set Control Mode / Change mode to Auto or Manual valve djustment	~XB=VST,DST=TRB,PT=SCM,M=1~	M: Mode, 0 = auto, 1 = manual
	BTN: Button Packet / Older packet type sent by controller unit; currently only implements valve stepping commands in turbine, reading A1 and A2	~XB=MUB,DST=TRB,PT=BTN,A1=1,A2=0,B1=0,B2=0~	A[12],B[12]: state of corresponding button on controller unit, 1 = depressed, 0= not; the TRB unit responds to A1 as step up, A2 as step down, ignores B[12].
	RST: Reset Packet	~XB=VST,DST=TRB,PT=RST~	Request a full reset from the turbine unit. Not any different than setting valves to ABC and mode to manual, except millis() timer is also reset.

Grid Tie Shed Packets	WTT: Watt Production Packet	~XB=MUB,PT=WTT,W=2576,T=11.2,Y=32.8~	W: Current power production in watts / T: kWh produced today (since midnight) / Y: total kWh produced yesterday

Sauna (Battery Room) Packets	PWR: Battery System Status Packet	~XB=SNA,PT=PWR,V=55.4,H=53.0,S=0,L=300~	V: Current battery voltage / H: hourly average voltage / L: Current system load in watts / S: Status codeused for indicator colors @ sauna, on controller, and in webserver; from 1 to-3; 1 = green (very good), 0 = OK -1 = not so good (solid red), -2 = bad (blinking red), -3 = critical (fast blinking red); these #s are calculated in the perl code on the laptop and are for A.Y.s reference.